COS Above Ceiling Punchlist

Biology 122

1. Insulate cold water piping
2. Install slack wire for speakers (Typical all locations)
3. Anchor registers and install slack wires
4. Splay wires not to be bent around ducting or piping
5. Make up wires and install cover plate at electrical junction box
6. 2 inch wall angle is wavy at window
7. 2 inch wall angle has gap at NE corner at tackboard
8. 2 inch wall angle has deflection in some areas which results in gap at wall
9. Install “flags” at shut-off valves?

Room 113 – OK

Room 116

1. Insulate mech hydronic piping
2. Install 2 screws per BERC clip

Biology Prep

1. Check main runner for wires every 4 feet (see making tape)
2. Missing splay wire at compression strut at center post east side
3. Remove and replace bent splay wire at center compression strut