COS Above Ceiling Punchlist 4

Room 110

1. Install hanger wire at trapeze (see masking tape)
2. Seismic splay wire cannot bend around ductwork. 4 locations where splay wire needs to be installed to wall or distant I joist
3. Electrical junction box in NW corner to have cover installed.

Ok to drop tiles in Rooms 103 & 105.