COS Above Ceiling Punchlist 5 2nd Floor

Room 216

1. Replace beam clamps at hydronic piping next to VAV. (Issue discussed with David)
2. All fume ducting to be strapped in tension (no slack)
3. Complete wall angle on east side (Install BERC clips)
4. Strap HVAC control wiring
5. Install additional hanger wires on south side of room…existing wire do not conform to 1/6 ratio requirement
6. Install additional hanger wires…max 4 OC see masking tape
7. Compression strut splay wires need to be in tension; typical
8. Some 4’ hanging wires do not meet 1/6 ratio; add wire in opposite direction or replace. See masking tape for locations.
9. Fix tears in FSK; all trades
10. Add compression strut to at east main runner in center of window
11. Compression struts along ridge are not correct size. See FCD 22.1.
12. Add splay wire to wall; see masking tape for location.

Room 217

1. Install register and slack wire
2. Refasten duct straps

Room 214

1. Install 2 screws in BERC clips
2. Trapeze installed does meet length requirements; See FCD 22.4
3. Install duct strapping at SW corner of room.

**No further inspections will be made until I have been notified that rooms have been reviewed for compliance by all trades.**