COS Above Ceiling Punchlist 7 2nd Floor

Room 215

1. Complete wall angle at window trim.
2. Compression strut not anchored to I-Joist; see masking tape
3. Repair FSK near window
4. Steel angle support and fume hood in contact (2 locations)
5. Add support of exhaust duct along north wall; see masking tape
6. Add support to return ductwork along north wall; see masking tape

Room 210

1. Repair FSK near window.

Room 212

Will inspect when wood trim is removed.